?.??	Semi Instantaneous Domestic Hot Water Generator

The Mechanical Contractor shall supply and install a semi instantaneous domestic hot water generator as supplied by CHWS Ltd (contact Sales, email: sales@chwsltd.co.uk tel: 01934 244 770) from their ProRapid range, in accordance with the following schedule:

- Model Reference:			ProRapid [Insert Model Reference]

- Vessel Capacity:			[Insert Capacity] litres

- Quantity: 				[Insert Quantity]

- Electrical Immersions:			[Insert kw input] [Insert quantity]

Plate Heat Exchanger Duty (Each):

[Insert kW input] kW @

[Insert Temperatures] Primary Flow & Return

[Insert Temperatures] Secondary Inlet / Outlet

The semi instantaneous DHW Generator shall strictly comprise the following features; suitable for domestic hot water generation, stainless steel construction, externally mounted WRAS approved brazed plate heat exchanger and secondary side DHW charging / destratification pump, pre-mounted on insulated copper pipe work, hard insultation finish, 6 bar working pressure, 100 Deg C maximum working temperature, 2x electrical immersion port, 4” inspection hatch, 3x ½” sensor tappings, temperature differential sensor for LTHW inlet, and integral control panel with full Bacnet functionality and remote monitoring.

The unit should be fully WRAS / KIWAUKReg4 approved.