?.??	Thermal Store / Heating Water Buffer Vessel

The Mechanical Contractor shall supply and install a thermal store / heating water buffer vessel, as supplied by Commercial Hot Water Solutions Ltd (contact sales, email: sales@chwsltd.co.uk tel: 01934 244 770) from their ProStor PS range, in accordance with the following schedule:-

- Model ref:				ProStor PS 1000

- Vessel Capacity:			1000 litres

- Service Connection Sizes:		6x 3”

The PS Heating Water Vessel shall strictly comprise the following features: high quality steel construction, 20mm close cell + 100mm Flexible Insulation with PVC Outer Jacket, 3x internal destratification baffles, inlet deflector plate to minimize inlet velocities and promote stratification, inspection hatch, electrical immersion port, 3x 1” top dished end connections and 6x ½ sensor tappings for temperature monitoring. The unit shall have a maximum working pressure of 6 bar, test pressure of 9 bar and a maximum working temperature of 95 Deg C.