?.??	Thermal Store / Heating Water Buffer Vessel

The Mechanical Contractor shall supply and install a thermal store / heating water buffer vessel, as supplied by Commercial Hot Water Solutions Ltd (contact sales, email: sales@chwsltd.co.uk tel: 01934 244 770) from their ProStor PS range, in accordance with the following schedule:

- Model Ref:				ProStor PS 800

- Vessel Capacity:			800 litres

- Service Connection Sizes:		6x 3”

The ProStor PS Heating Water Vessel shall strictly comprise the following features: S235JR mild steel construction, 100mm PO Flex Insulation with PVC Outer Jacket, 3x internal destratification baffles, 2x linear sparge pipes, inspection hatch, electrical immersion port, 3x ¾” top dished end connections and 7x ½ sensor tappings. The unit shall be externally painted with an anti-corrosion primer, have a maximum working pressure of 6 bar, test pressure of 9 bar and a maximum working temperature of 95 Deg C.

The ProStor PS range of mild steel buffer vessels are suitable for the storage of heating / primary side water. This range is covered by the following standards:

- Manufactured in accordance with PED 2014/68/EU

- UKCA/CE Certified

- Manufactured in an ISO 9001 product & process quality accredited facility