?.??	Thermal Store / Heating Water Buffer Vessel

The Mechanical Contractor shall supply and install a thermal store / heating water buffer vessel, as supplied by Commercial Hot Water Solutions Ltd (contact sales, email: sales@chwsltd.co.uk tel: 01934 244 770) from their ProStor PS range, in accordance with the following schedule:-

- Model ref:				ProStor PS 100

- Vessel Capacity:			94 litres

- Service Connection Sizes:		1 ½”

The PS Heating Water Vessel shall strictly comprise the following features: high quality steel construction, 70mm flexible insulation with PVC Outer Jacket, 3x internal destratification baffles, inlet deflector plate to minimize inlet velocities and promote stratification, electrical immersion port, 3x ½” top dished end connections and 6x ½ sensor tappings for temperature monitoring. The unit shall have a maximum working pressure of 6 bar, test pressure of 9 bar and a maximum working temperature of 95 Deg C.